## Sheet1
UV Dose Calculator using the Keitz equation: Irradiance (E) = P/(2LDπ²)*(2α+Sin2α). This table will calculate the UVc dose at the midpoint between the quartz tube and chamber wall. Note that the UVc emmited by the lamp is not the same as its standard power consumption rating, you need to look up the lamp specifications to find this.
System Info |  |  |  | Input parameters | [8 empty] | Formulae | [7 empty] | Output
System description |  | UV model | Lamp model | UVc output of lamp (watts) | Lamp arc length (cm) | Inner diameter of chamber (cm) | Outer diameter of quartz tube (cm) | Water volume of unit (litres) as measured directly | Number of units | Total volume of units (litres) | Flow rate (litres per minute) | *Optional*Max system volume (litres) | UV contact time (seconds) | Distance from quartz tube to chamber wall (cm) | Arc length of lamp (meters) (L) | Midpoint between quartz tube and chamber wall) (meters) (D) | UVc power (watts) (P) | ArcTan L/2D (α) | Dose (Watts/m²) (E) | Dose µWatt/cm² | Total dose (µJ/cm²) new lamp | Total dose (µJ/cm²) end of lamp life (1 year, 80% UV power) | System turnover rate per hour
Sanger system UV's | Max system flow (according to flow meters) | TMC commercial P1 55 | G55T8 | 18 | 84 | 5.65 | 3 | 1.25 | 4 | 5 | 138 | 1800 | 2.1739 | 1.325 | 0.84 | 0.021625 | 18 | 1.5194 | 157.7002 | 15770.0168 | 34282.6451 | 27426.1161 | 4.6
Blue system killifish C3 | Current system flow | TMC Vecton Titan 850 | G25T8 | 6.9 | 40 | 4.6 | 3 | 0.3 | 1 | 0.3 | 16 | 300 | 1.125 | 0.8 | 0.4 | 0.019 | 6.9 | 1.4761 | 144.4439 | 14444.392 | 16249.941 | 12999.9528 | 3.2
Central services storage tanks | ST01 pump @ 5m head | Custom | TUV PL-L 55W | 17 | 49 | 8.375 | 4.99 | 2.25 | 1 | 2.25 | 320 | 20000 | 0.42188 | 1.6925 | 0.49 | 0.033412 | 17 | 1.4353 | 165.0846 | 16508.4565 | 6964.5051 | 5571.6041 | 0.96
| ST03 pump @ 5m head | Custom | TUV PL-L 55W | 17 | 49 | 8.375 | 4.99 | 2.25 | 1 | 2.25 | 310 | 7000 | 0.43548 | 1.6925 | 0.49 | 0.033412 | 17 | 1.4353 | 165.0846 | 16508.4565 | 7189.1665 | 5751.3332 | 2.6571
| ST04 pump @ 5m head | Custom | TUV PL-L 55W | 17 | 49 | 8.375 | 4.99 | 2.25 | 1 | 2.25 | 310 | 7000 | 0.43548 | 1.6925 | 0.49 | 0.033412 | 17 | 1.4353 | 165.0846 | 16508.4565 | 7189.1665 | 5751.3332 | 2.6571
| ST05 pump @ 5m head | Custom | TUV PL-L 55W | 17 | 49 | 8.375 | 4.99 | 2.25 | 1 | 2.25 | 180 | 7000 | 0.75 | 1.6925 | 0.49 | 0.033412 | 17 | 1.4353 | 165.0846 | 16508.4565 | 12381.3424 | 9905.0739 | 1.5429
EMFF A | All tanks at suggested flow rate | Sita UV PE 5 | 75 watt t5 UVc | 25 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 144 | 5000 | 2.2917 | 3.95 | 0.775 | 0.03125 | 25 | 1.4903 | 164.2527 | 16425.2686 | 37641.2406 | 30112.9925 | 1.728
EMFF B | All tanks at suggested flow rate | Sita UV PE 5 | 75 watt t5 UVc | 25 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 80 | 5000 | 4.125 | 3.95 | 0.775 | 0.03125 | 25 | 1.4903 | 164.2527 | 16425.2686 | 67754.2331 | 54203.3865 | 0.96
Tropical | All tanks at suggested flow rate | Sita UV PE 5 | 75 watt t5 UVc | 25 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 118 | 5000 | 2.7966 | 3.95 | 0.775 | 0.03125 | 25 | 1.4903 | 164.2527 | 16425.2686 | 45935.0733 | 36748.0586 | 1.416
Ornamental | All tanks at suggested flow rate | Sita UV PE 3 | 75 watt t5 UVc | 15 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 88 | 5000 | 3.75 | 3.95 | 0.775 | 0.03125 | 15 | 1.4903 | 98.5516 | 9855.1612 | 36956.8544 | 29565.4835 | 1.056
Twin A | All tanks at suggested flow rate | Sita UV PE 3 | 75 watt t5 UVc | 15 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 99.6 | 5000 | 3.3133 | 3.95 | 0.775 | 0.03125 | 15 | 1.4903 | 98.5516 | 9855.1612 | 32652.6425 | 26122.114 | 1.1952
Twin B | All tanks at suggested flow rate | Sita UV PE 3 | 75 watt t5 UVc | 15 | 77.5 | 10.2 | 2.3 | 5.5 | 1 | 5.5 | 99.6 | 5000 | 3.3133 | 3.95 | 0.775 | 0.03125 | 15 | 1.4903 | 98.5516 | 9855.1612 | 32652.6425 | 26122.114 | 1.1952